### Comparison Between IEC 69896-1 & IEC 60947-2

| MCB / MCCB Characteristic | IEC 60898-1 | IEC 60947-2 |
| --- | --- | --- |
| Rated Current: In | 6 – 125A | 0.5 – 160A |
| SC Breaking Capacity | <25kA | <50kA |
| Rated Voltage: Ue | 400V | 440V 500V, 690V |
| Impulse Voltage: Uimp | 4kV | 6kV – 8kV |
| Pollution Degree | 2 | 3 |
| Curves | B,C,D | B,C,D,K,Z,MA |
| Application Current | AC | AC or DC |
| Electrical Auxiliaries | No | Monitoring Control |